CODESYS–Factory I/O OPC UA Integration — Troubleshooting Retrospective

Authentication policy mismatch and stale OPC UA node mapping

| Context | Simulated conveyor-sorting integration |
| --- | --- |
| Environment | CODESYS Control Win V3 ↔ OPC UA ↔ Factory I/O |
| Scope | Local simulation only; no physical PLC, control panel, or production system |

# Executive Summary

During integration of a CODESYS Control Win SoftPLC with Factory I/O over OPC UA, I faced two issues that prevented the official sorting sample from running:

- First, the Factory I/O client could not authenticate against the runtime's newly enforced device-user policy;

- Second, after authentication was corrected, the scene raised a null-object exception because its saved OPC UA mappings were no longer usable.

The issues were resolved through a scoped local-simulation security configuration and a clean rebuild of all 18 tag mappings; the scene then connected and operated normally, with no production or customer impact.

# Issue #1 – Discovery

## How It Was Detected

- Detection method: manual integration check during Online → Login in CODESYS and subsequent connection from the Factory I/O driver.

- CODESYS first prompted that the runtime enforced device user management. An administrator account was created as part of first-time runtime initialization.

- Factory I/O then failed during the OPC UA connection attempt with an identity/authentication-related error rather than reaching normal tag exchange.

## Initial Symptoms and Misdiagnoses

- Initial symptom: the SoftPLC application could run in CODESYS, but Factory I/O could not establish a usable OPC UA session.

- Early possibilities included port 4840 conflict, a stopped SoftPLC, missing symbols, a certificate problem, or an incorrect endpoint.

- As a starter, I made a procedural misstep: looking for synchronization controls on Communication Settings. Those controls belong to Access Rights, so the absence of the button on the first page was expected, not a product fault.

- The first prompt was initially described too loosely as an error. It was actually a security-initialization requirement; the integration failure occurred later when the legacy sample attempted an identity mode that the runtime policy did not accept.

# Issue #1 – Root Cause Analysis

## Technical Chain of Events

- A current CODESYS Control Win runtime was started for the first time and enforced device user management.

- An administrator account was created, making authenticated device access mandatory under the active runtime security policy.

- The official Factory I/O sample attempted to connect to opc.tcp://localhost:4840 using its saved/default anonymous OPC UA identity flow.

- The OPC UA server rejected that identity before the client could establish a fully usable session and consume the published PLC symbols.

- Because the failure occurred at the authentication/authorization boundary, changing PLC logic or Factory I/O tag mappings could not have solved this stage.

## Why It Happened — Systemic Gaps

- Version drift: the official sample's assumptions were older than the security defaults in the installed CODESYS runtime.

- Hidden prerequisite: device-user initialization and OPC UA anonymous permissions were not part of the initial setup checklist.

- Layer ambiguity: CODESYS engineering login, runtime device users, OPC UA identities, symbol publication, and Factory I/O mappings are separate controls but appeared in one end-to-end workflow.

- Diagnostic gap: the initial plan lacked explicit checkpoints for endpoint reachability, authentication, namespace browsing, mapping validity, and functional behavior.

# Issue #1 – Fix & Validation

## Exact Action Taken

- In CODESYS, opened Device → Change Runtime Security Policy....

- Set Device User Management to Optional user management and enabled Allow anonymous login for the local simulation runtime.

- Opened Access Rights and granted the Anonymous_OPCUAServer identity the required View, Modify, and Execute permissions under RemoteConnections → OPCUAServer.

- Kept the administrator account in place; no credentials were committed to Git or embedded in screenshots.

- Rebuilt/re-downloaded the PLC application as needed, returned it to RUN, and retried the Factory I/O connection.

## Validation

- Factory I/O progressed beyond the identity error and reached the OPC UA namespace.

- The client successfully browsed 18 published FIO variables, proving endpoint reachability, server availability, authentication acceptance, and symbol publication.

- Validation was performed as a layered integration test, not by assuming that a green PLC state alone proved end-to-end connectivity.

## Rollback / Production-Safe Alternative

- Rollback: restore required user management, disable anonymous login, and revoke the anonymous OPC UA rights.

- For a real industrial network, prefer a compatible authenticated OPC UA client, least-privilege permissions, certificate validation, and network segmentation. The anonymous setting was intentionally scoped to a single-machine simulation and should not be copied into production.

# Issue #2 – Discovery

## How It Was Detected

- Detection method: manual driver check immediately after Issue #1 was cleared.

- Factory I/O displayed Object reference not set to an instance of an object while loading or applying the saved OPC UA configuration.

- At the same time, the driver could browse and display 18 CODESYS variables, which became the decisive diagnostic clue.

## Initial Symptoms and Misdiagnoses

- The generic null-object message initially left certificate, access-right, port, and Symbol Configuration failures in scope.

- The successful 18-variable browse falsified most of those hypotheses: the endpoint, OPC UA server, authentication path, and symbol exposure were already functioning.

- The investigation therefore moved one layer higher—from transport/authentication to the Factory I/O scene's persisted node references and tag bindings.

# Issue #2 – Root Cause Analysis

## Technical Chain of Events

- The official .factoryio scene contained saved mappings to OPC UA nodes from the environment in which the sample was originally authored.

- The current CODESYS SP22-era runtime generated or exposed a valid namespace, but one or more saved references in the scene did not resolve to the current browsed node objects.

- Factory I/O attempted to dereference a missing/stale mapped object and surfaced a generic .NET-style null-reference exception.

- Clearing the saved mappings, browsing the live namespace, and rebuilding all mappings removed the invalid references; the same PLC program and endpoint then worked.

## Root-Cause Confidence

This is a high-confidence inference, not a vendor-confirmed defect classification. It is supported by the observable sequence: live namespace browsing succeeded, the error survived until persisted mappings were cleared, and normal operation returned after mapping against the current namespace.

## Why It Happened — Systemic Gaps

- Serialized integration state was treated as portable even though OPC UA NodeIds and client-side references can vary by runtime/sample version.

- The sample did not fail with a precise message such as “mapped node not found”; its null-reference error obscured the failing layer.

- The setup process had no compatibility check comparing saved mappings with the live namespace before connection.

- A sample project was initially treated as a known-good baseline, although samples are dependencies that also require version validation.

# Issue #2 – Fix & Validation

## Exact Action Taken

- Saved the Factory I/O scene as a new copy to preserve a recoverable original.

- Disconnected the driver and used CLEAR to remove only the scene's stale mappings; no PLC code or CODESYS symbols were deleted.

- Browsed opc.tcp://localhost:4840 with a filter for FIO and confirmed the current set of 18 variables.

- Recreated the sensor/input mappings to iAtEntry, iLowBox, iHighBox, iAtTurnEntry, iAtLoadPos, iAtUnloadPos, iAtFront, iAtRightEntry, iAtLeftEntry, iAtRightExit, and iAtLeftExit.

- Recreated the actuator/output mappings to oFeederConveyor, oEntryConveyor, oLoad, oUnload, oTurn, oLeftConveyor, and oRightConveyor.

- Reconnected the driver and returned Factory I/O to RUN mode.

## Validation

- The null-reference exception no longer appeared.

- The driver retained all 18 live bindings and the scene operated normally.

- Functional validation confirmed that the PLC-to-simulation path—not merely namespace browsing—was working end to end.

## Rollback

- Reopen the untouched original scene or the pre-change copy. Because CLEAR only changed client-side scene mappings, rollback did not require restoring the PLC application.

# Interdependencies

- The issues were correlated by sequence, not by a shared root cause.

- Issue #1 blocked the OPC UA authentication boundary and therefore masked Issue #2. The stale-mapping failure became visible only after the client could browse the server.

- Issue #1 did not create the stale mappings. Its resolution simply advanced the connection far enough to expose the next latent incompatibility.

- This is a classic stacked-failure pattern: fixing one valid blocker can reveal another without invalidating the first diagnosis.

# Key Learnings

- Troubleshoot integrations by layer: runtime state → endpoint/port → identity → authorization → symbol publication → namespace browse → mapping → functional sequence.

- A successful namespace browse is strong evidence: it rules out many lower-layer failures but does not prove saved mappings or machine behavior.

- Treat generic exceptions as symptoms. Use surrounding positive evidence to identify the highest layer already known to work.

- Security defaults change across versions. A tutorial's authentication assumptions must be verified, not inherited blindly.

- Preserve a rollback copy before clearing opaque or serialized client configuration.

- Keep local simulation exceptions explicit and scoped; do not normalize anonymous access as a production pattern.

- Correct imprecise guidance quickly. Knowing which CODESYS page owns a control is part of operational accuracy.

- Record inference confidence. Honest uncertainty is stronger engineering practice than overstating an unconfirmed vendor root cause.

# What We Would Do Differently

- Start with a five-gate checklist: SoftPLC RUN, endpoint reachable, identity accepted, expected symbol count browsable, functional I/O observed.

- Capture the exact error text and timestamp at first occurrence instead of relying on memory or paraphrase.

- Read the version-specific CODESYS/Factory I/O setup notes before applying an older sample to a newer runtime.

- Save a clean scene copy before the first connection attempt and expect to rebuild persisted mappings when versions differ.

- Change one layer at a time and record the new evidence after each change; avoid simultaneous security, symbol, and mapping edits.

- After recovery, add a repeatable smoke test: reconnect from a cold start, verify all 18 tags, and run at least one complete sort cycle.